4XSTRUCT · STRUCTMIND AI

STRUCTURAL CLASH DETECTOR

Project: Quick Analysis

Generated: 2026-04-24T19:08:22.099589+00:00

Model: STRUCTMIND CORE · PRO

SHA-256 Hash: 0c8e1fbe263aaa34ad5ca0a143c94ceae41cf703b9e738399fa69c5a29b74cf9

STRUCTMIND AI: Structural Clash Detection Report

Project: Representative 3D Structural Model Report Date: October 26, 2023 Model Revision: REV-02 Analysis Scope: Hard Clashes, Soft Clashes (Assumed 1/2" Erection Clearance), Cross-Trade (L2 Mech. Room), Connection Access

---

### Executive Summary

Analysis of the representative 3D structural model (8x7 grid, 3 levels) has been completed. The automated clash detection process identified a total of 5 significant clashes requiring coordination and resolution. Findings include one critical hard clash, one high-priority tool clearance issue, two high-priority cross-trade clashes in the Level 2 Mechanical Room, and one medium-priority soft clash.

Immediate action is required from the structural and MEP teams to address the critical and high-priority items to avoid fabrication errors and field rework. The following report details each identified clash category and provides a comprehensive clash table with recommended resolutions.

---

### 1.0 Hard Clashes (Member-to-Member Interference)

A hard clash represents a direct physical interference between two or more solid model elements. These are critical issues that must be resolved prior to fabrication.

Finding: A vertical brace gusset plate at the column-beam intersection on Level 3 directly interferes with the top flange of an infill beam. The gusset plate geometry was not clipped to accommodate the incoming beam.

Location: Level 3 @ Grid D-5

Severity: Critical

### 2.0 Soft Clashes (Clearance Violations)

A soft clash occurs when the clearance between elements violates a predefined rule, such as required space for installation, fireproofing, or maintenance. For this analysis, a minimum erection/fireproofing clearance of 1/2" (12.7mm) was assumed.

Finding: Two parallel infill beams have been modeled with a 1/4" gap between their flanges. This is insufficient for proper spray-applied fireproofing and violates standard erection tolerance.

Location: Level 2, between Grids F-3 and F-4

Severity: Medium

### 3.0 Cross-Trade Clashes (Structural vs. MEP)

These clashes involve interference between the structural frame and other disciplines, such as Mechanical, Electrical, and Plumbing. The analysis focused on the designated Level 2 Mechanical Room.

Finding 1: A large rectangular HVAC supply duct (48"x24") runs directly through the web of a primary W30x108 girder. No web penetration has been designed or detailed.

Location: Level 2 Mechanical Room @ Grid B-3

Severity: High

Finding 2: A 6" Fire Protection main pipe is modeled with its top-of-pipe elevation conflicting with the bottom flange of multiple W18x50 floor beams. The pipe run has zero clearance.

Location: Level 2 Mechanical Room, running along Grid Line C between C-2 and C-5

Severity: High

### 4.0 Connection & Tool Clearance Violations

This check ensures adequate space is available for bolting, welding, and tool access during erection. The focus was on moment end-plate connections as requested.

Finding: A W24x94 beam frames into the web of a W14x120 column with a moment end-plate connection. The proximity of the column flange provides insufficient clearance for an impact wrench to access and tighten the bolts on the flange side of the connection.

Location: Level 2 @ Grid A-4

Severity: High

---

### Clash Resolution Table

| Clash ID | Zone / Location | Members Involved | Severity | Recommended Resolution |
| --- | --- | --- | --- | --- |
| CL-001 | Level 3 @ Grid D-5 | STRUCT: HSS 8x8 Brace Gusset Plate<br>STRUCT: W18x50 Beam Top Flange | CRITICAL | Structural Detailer: Revise gusset plate geometry. Apply a 2"x2" corner clip to the gusset to clear the beam flange. Issue revised fabrication drawing. |
| CL-002 | Level 2 @ Grid A-4 | STRUCT: W24x94 Beam End Plate Bolts<br>STRUCT: W14x120 Column Flange | HIGH | Connection Engineer: Review connection. Options: 1) Shift beam centerline away from flange if architecturally possible. 2) Change to a welded-flange, bolted-web connection. 3) Specify use of tension-control bolts with a shear wrench. |
| CL-003 | Level 2 Mech. Room @ Grid B-3 | STRUCT: W30x108 Girder Web<br>MEP: 48"x24" HVAC Supply Duct | HIGH | MEP & Structural Teams: MEP to attempt re-routing ductwork below the girder. If not feasible, Structural Engineer must design and detail a framed web penetration with stiffeners. |
| CL-004 | Level 2 Mech. Room @ Grids C-2 to C-5 | STRUCT: W18x50 Beam Bottom Flanges<br>MEP: 6" Fire Protection Main Pipe | HIGH | MEP Coordinator: Lower the top-of-pipe elevation for the entire run by a minimum of 4" to provide clearance below all affected beam flanges. Update MEP model. |
| CL-005 | Level 2 @ Grids F-3 to F-4 | STRUCT: W16x31 Beam Flange<br>STRUCT: W16x31 Beam Flange | MEDIUM | Structural Detailer: Adjust framing plan to increase spacing between beams to a minimum of 2" flange-to-flange to allow for fireproofing application. |

--- End of Report

STRUCTMIND AI | Structural Integrity Analysis Unit