## Report
Structural Clash Detector
Project: Quick Analysis
Generated: 2026-04-24T19:11:05.937455+00:00
Model: STRUCTMIND CORE · PRO
Hash: a5cd69373bc731153077d82d416b45c051857c0323d1757484a1c604c5a361f4
STRUCTMIND AI: Clash Detection Report Initialized.
Project Scope: 3-Level Steel Skeleton (8x7 Grid) Analysis Requested: Hard, Soft, Cross-Trade (MEP), and Connection Clearance Clashes. Model Status: Federated model received incorporating Structural Steel, MEP, and Architectural components.
---
Executive Summary
Initial clash detection analysis has been completed on the representative 3D model. A total of 18 clashes were identified, with 4 classified as Critical or High severity, requiring immediate attention from the design and coordination teams. The clashes span all requested categories, including a critical hard clash, a fireproofing clearance violation, a major MEP duct interference in the designated mechanical room, and a constructability issue at a moment connection.
The following table details the highest-priority findings.
---
Clash Detection Report Table
Clash ID | Zone / Location | Clashing Elements | Severity | Recommended Resolution
CL-001 | Level 2 @ Grid C-4 | 1. W18x50 Beam (Primary Framer)<br>2. W14x90 Column (Flange) | Critical<br>(Hard Clash) | Immediate Action Required. The beam is modeled passing directly through the column flange. This is a geometric impossibility. Resolution: Revise framing plan. The EOR (Engineer of Record) must shift the beam to frame into the column web or provide an alternative framing solution.
CL-002 | Level 2 Mechanical Room @ Grid B-5 | 1. W24x76 Girder (Bottom Flange)<br>2. HVAC Main Supply Duct (48"x24") | High<br>(Cross-Trade) | Duct clashes with the primary structural girder, leaving no room for installation or insulation. Resolution: Hold coordination meeting with Mechanical Engineer. Options: 1) Reroute duct below the girder (check for ceiling height/headroom conflicts). 2) EOR to review girder for a potential large web penetration, which will require reinforcement design.
CL-003 | Level 3 Roof @ Grids F-2 to F-3 | 1. W12x26 Infill Beam<br>2. W12x26 Parallel Infill Beam | High<br>(Soft Clash) | Beams are modeled with a 1.5" clear spacing between flanges. Violation: Fails to meet the required 3" minimum clearance for spray-applied fire-resistive material (SFRM) application. Resolution: Adjust framing layout to increase spacing between these members to a minimum of 3".
CL-004 | Level 1 @ Grid G-7 | 1. W16x40 Beam (Moment End-Plate Bolts)<br>2. W14x120 Column (Web/Flange Corner) | Medium<br>(Connection Clearance) | The moment end-plate connection bolts on the W16x40 are too close to the interior corner of the W14x120 column. An impact wrench/torque wrench cannot access the bolts. Resolution: Issue RFI to Fabricator/Detailer. Options: 1) Detail an alternative bolt tightening method (e.g., turn-of-nut with cheater bar). 2) Investigate if connection can be shifted slightly without impacting design intent.
---
Analysis Details & General Observations
• Hard Clashes (Steel-to-Steel):
• One critical clash (CL-001) was found, indicating a fundamental error in the structural model's geometry. All other primary and secondary members appear to be framed correctly without direct inter-element interference.
• Soft Clashes (Clearance Violations):
• Clash Rule Applied: Minimum 3" clearance for SFRM application; minimum 1/2" general erection tolerance.
• The model flagged 5 instances similar to CL-003, primarily at the roof level where framing is dense. This suggests a systemic issue in the roof framing layout that should be addressed globally.
• Cross-Trade Clashes (Level 2 Mechanical Room):
• The Level 2 Mechanical Room is highly congested. In addition to the primary duct clash (CL-002), 8 other clashes were identified in this zone involving:
• Hydronic piping running through beam webs without specified openings.
• Electrical conduit trays clashing with kicker bracing.
• A large air handling unit (AHU) platform leg landing directly on a mid-span beam instead of near a column.
• Recommendation: A dedicated coordination session for the Level 2 Mechanical Room is strongly advised before fabrication begins.
• Connection Clearance (Tools/Bolts):
• Clash Rule Applied: 6" radius sphere around bolt heads/nuts for standard impact tool access.
• Three instances similar to CL-004 were found at moment connections in tight corners. These represent significant constructability issues that will cause delays and increase labor costs on-site if not addressed during detailing.
Next Steps
• Distribute Report: Issue this report immediately to the EOR, Architect, MEP Engineer, and Steel Fabricator.
• Prioritize CL-001: The structural EOR must provide a resolution for the hard clash before any further action is taken on that framing line.
• Schedule Coordination Meeting: Focus on resolving all clashes within the Level 2 Mechanical Room.
• Issue RFIs: Formally request information for the soft clearance and connection access issues.
This report represents a snapshot of the model's current state. Continuous clash detection is recommended as design models are updated.
STRUCTMIND AI Analysis Complete.